{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["6月上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2024.06.03","锦绣花城社区","20240603-461",16,"未检出","<5","0.31","无","无",0.04,{"v":1.4,"d":"1.40"},"2024.06.05"," 王晓芳"]
[2,"2024.06.03","市自来水公司铝城营业所","20240603-462",7,"未检出","<5","0.30","无","无",0.05,"/","2024.06.05"," 王晓芳"]
[3,"2024.06.03","经开区后南定村卫生室","20240603-463","未检出","未检出","<5","0.29","无","无",0.04,"/","2024.06.05"," 王晓芳"]
[4,"2024.06.03","市自来水公司南定营销服务中心","20240603-464","未检出","未检出","<5","0.45","无","无",0.05,1.42,"2024.06.05"," 王晓芳"]
[5,"2024.06.03","张南路101号中石油加油站","20240603-465",3,"未检出","<5","0.15","无","无",0.04,"/","2024.06.05"," 王晓芳"]
[6,"2024.06.03","西苑社区","20240603-466",8,"未检出","<5","0.24","无","无",0.03,"/","2024.06.05"," 王晓芳"]
[7,"2024.06.04","高新区金晶大道汇驰奔驰4S店","20240604-467",4,"未检出","<5","0.26","无","无",0.04,"/","2024.06.06"," 王晓芳"]
[8,"2024.06.04","金都花园社区","20240604-468",7,"未检出","<5","0.32","无","无",0.03,1.23,"2024.06.06"," 王晓芳"]
[9,"2024.06.04","外商居住区","20240604-469",10,"未检出","<5","0.38","无","无",0.04,"/","2024.06.06"," 王晓芳"]
[10,"2024.06.04","星悦城社区","20240604-470",9,"未检出","<5","0.45","无","无",0.05,1.31,"2024.06.06"," 王晓芳"]
[11,"2024.06.05","淄博市委","20240605-471",2,"未检出","<5","0.28","无","无",0.05,"/","2024.06.07"," 王晓芳"]
[12,"2024.06.05","张店区军休所","20240605-472",5,"未检出","<5","0.30","无","无",0.04,"/","2024.06.07"," 王晓芳"]
[13,"2024.06.05","五里桥生活区","20240605-473",13,"未检出","<5","0.27","无","无",0.05,"/","2024.06.07"," 王晓芳"]
[14,"2024.06.05","张店八中","20240605-474",8,"未检出","<5","0.24","无","无",0.06,"/","2024.06.07"," 王晓芳"]
[15,"2024.06.05","积家村党群服务中心","20240605-475",41,"未检出","<5","0.26","无","无",0.03,1.29,"2024.06.07"," 王晓芳"]
[16,"2024.06.05","明德苑社区","20240605-476",29,"未检出","<5","0.27","无","无",0.03,"/","2024.06.07"," 王晓芳"]
[17,"2024.06.05","淄博市图书馆","20240605-477",18,"未检出","<5","0.23","无","无",0.04,"/","2024.06.07"," 王晓芳"]
[18,"2024.06.06","恒嘉园社区","20240606-478",3,"未检出","<5","0.25","无","无",0.06,"/","2024.06.08"," 王晓芳"]
[19,"2024.06.06","人民东路小学","20240606-479",7,"未检出","<5","0.23","无","无",0.05,"/","2024.06.08"," 王晓芳"]
[20,"2024.06.06","张店区保安公司","20240606-480",5,"未检出","<5","0.24","无","无",0.05,"/","2024.06.08"," 王晓芳"]
[21,"2024.06.06","润德实业公司","20240606-481",3,"未检出","<5","0.20","无","无",0.06,"/","2024.06.08"," 王晓芳"]
[22,"2024.06.06","行政执法局湖田中队","20240606-482",5,"未检出","<5","0.22","无","无",0.04,"/","2024.06.08"," 王晓芳"]
[23,"2024.06.06","淄博市公交东站","20240606-483",3,"未检出","<5","0.19","无","无",0.04,"/","2024.06.08"," 王晓芳"]
[24,"2024.06.06","洪三社区","20240606-484",9,"未检出","<5","0.36","无","无",0.03,1.35,"2024.06.08"," 王晓芳"]
[25,"2024.06.11","新村西路140号原市水资办","20240611-485",15,"未检出","<5",0.27,"无","无",0.03,"/","2024.06.13"," 王晓芳"]
[26,"2024.06.11","张店区疾控中心","20240611-486",7,"未检出","<5","0.21","无","无",0.04,"/","2024.06.13"," 王晓芳"]
[27,"2024.06.11","淄博市政务中心","20240611-487","未检出","未检出","<5","0.24","无","无",0.05,"/","2024.06.13"," 王晓芳"]
[28,"2024.06.11","盛世康城社区","20240611-488",10,"未检出","<5","0.25","无","无",0.03,"/","2024.06.13"," 王晓芳"]
[29,"2024.06.12","淄博市工商局","20240612-489",5,"未检出","<5","0.30","无","无",0.04,"/","2024.06.14"," 王晓芳"]
[30,"2024.06.12","科技苑物业","20240612-490","未检出","未检出","<5","0.33","无","无",0.06,"/","2024.06.14"," 王晓芳"]
[31,"2024.06.12","瑞丰苑社区","20240612-491",6,"未检出","<5","0.29","无","无",0.03,2.31,"2024.06.14"," 王晓芳"]
[32,"2024.06.12","市自来水公司新区营业所","20240612-492",3,"未检出","<5","0.31","无","无",0.04,"/","2024.06.14"," 王晓芳"]
[33,"2024.06.12","祥瑞花园社区","20240612-493",15,"未检出","<5","0.32","无","无",0.04,"/","2024.06.14"," 王晓芳"]
[34,"2024.06.12","世纪花园社区","20240612-494",21,"未检出","<5","0.34","无","无",0.05,"/","2024.06.14"," 王晓芳"]
[35,"2024.06.12","颐臻园社区","20240612-495",10,"未检出","<5","0.29","无","无",0.03,"/","2024.06.14"," 王晓芳"]
[36,"2024.06.13","淄博市体育馆","20240613-496",9,"未检出","<5","0.31","无","无",0.04,"/","2024.06.15"," 王晓芳"]
[37,"2024.06.13","福源汇社区","20240613-497",17,"未检出","<5","0.25","无","无",0.05,"/","2024.06.15"," 王晓芳"]
[38,"2024.06.13","孝妇河湿地公园喷泉广场","20240613-498",10,"未检出","<5","0.31","无","无",0.05,2.81,"2024.06.15"," 王晓芳"]
[39,"2024.06.13","石家社区","20240613-499",15,"未检出","<5","0.33","无","无",0.04,2.57,"2024.06.15"," 王晓芳"]
[40,"2024.06.13","山泉路启星比亚迪4S店","20240613-500",9,"未检出","<5","0.29","无","无",0.03,"/","2024.06.15"," 王晓芳"]
[41,"2024.06.13","福瑞家园社区","20240613-501",35,"未检出","<5","0.27","无","无",0.03,2.61,"2024.06.15"," 王晓芳"]
[42,"2024.06.14","天勤苑社区","20240614-502",10,"未检出","<5","0.26","无","无",0.06,2.86,"2024.06.16"," 王晓芳"]
[43,"2024.06.14","市自来水开发区营业所","20240614-503",11,"未检出","<5","0.17","无","无",0.04,"/","2024.06.16"," 王晓芳"]
[44,"2024.06.14","淄博市十一中","20240614-504",17,"未检出","<5","0.27","无","无",0.04,"/","2024.06.16"," 王晓芳"]
[45,"2024.06.14","丽莎会议中心","20240614-505",20,"未检出","<5","0.29","无","无",0.03,"/","2024.06.16"," 王晓芳"]
[46,"2024.06.14","华侨城警务室","20240614-506",9,"未检出","<5","0.27","无","无",0.05,"/","2024.06.16"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}