{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["6月下半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2024.06.17","锦绣花城社区","20240617-507",11,"未检出","<5","0.30","无","无",0.05,2.37,"2024.06.19"," 王晓芳"]
[2,"2024.06.17","市自来水公司铝城营业所","20240617-508",3,"未检出","<5","0.28","无","无",0.06,"/","2024.06.19"," 王晓芳"]
[3,"2024.06.17","经开区后南定村卫生室","20240617-509",1,"未检出","<5","0.30","无","无",0.05,"/","2024.06.19"," 王晓芳"]
[4,"2024.06.17","市自来水公司南定营销服务中心","20240617-510","未检出","未检出","<5","0.33","无","无",0.06,2.69,"2024.06.19"," 王晓芳"]
[5,"2024.06.17","张南路101号中石油加油站","20240617-511",4,"未检出","<5","0.17","无","无",0.05,"/","2024.06.19"," 王晓芳"]
[6,"2024.06.17","西苑社区","20240617-512",6,"未检出","<5","0.26","无","无",0.04,"/","2024.06.19"," 王晓芳"]
[7,"2024.06.18","高新区金晶大道汇驰奔驰4S店","20240618-513",6,"未检出","<5","0.27","无","无",0.05,"/","2024.06.20"," 王晓芳"]
[8,"2024.06.18","金都花园社区","20240618-514",2,"未检出","<5","0.30","无","无",0.04,2.32,"2024.06.20"," 王晓芳"]
[9,"2024.06.18","外商居住区","20240618-515",7,"未检出","<5","0.29","无","无",0.05,"/","2024.06.20"," 王晓芳"]
[10,"2024.06.18","星悦城社区","20240618-516",5,"未检出","<5","0.35","无","无",0.04,2.49,"2024.06.20"," 王晓芳"]
[11,"2024.06.19","淄博市委","20240619-517","未检出","未检出","<5","0.27","无","无",0.06,"/","2024.06.21"," 王晓芳"]
[12,"2024.06.19","张店区军休所","20240619-518",3,"未检出","<5","0.29","无","无",0.05,"/","2024.06.21"," 王晓芳"]
[13,"2024.06.19","五里桥生活区","20240619-519",9,"未检出","<5","0.31","无","无",0.04,"/","2024.06.21"," 王晓芳"]
[14,"2024.06.19","张店八中","20240619-520",7,"未检出","<5","0.25","无","无",0.04,"/","2024.06.21"," 王晓芳"]
[15,"2024.06.19","积家村党群服务中心","20240619-521",51,"未检出","<5","0.28","无","无",0.04,2.25,"2024.06.21"," 王晓芳"]
[16,"2024.06.19","明德苑社区","20240619-522",35,"未检出","<5","0.25","无","无",0.02,"/","2024.06.21"," 王晓芳"]
[17,"2024.06.19","淄博市图书馆","20240619-523",21,"未检出","<5","0.21","无","无",0.05,"/","2024.06.21"," 王晓芳"]
[18,"2024.06.20","恒嘉园社区","20240620-524",6,"未检出","<5","0.23","无","无",0.05,"/","2024.06.22"," 王晓芳"]
[19,"2024.06.20","人民东路小学","20240620-525",2,"未检出","<5","0.24","无","无",0.04,"/","2024.06.22"," 王晓芳"]
[20,"2024.06.20","张店区保安公司","20240620-526",7,"未检出","<5","0.25","无","无",0.04,"/","2024.06.22"," 王晓芳"]
[21,"2024.06.20","润德实业公司","20240620-527",5,"未检出","<5","0.22","无","无",0.05,"/","2024.06.22"," 王晓芳"]
[22,"2024.06.20","行政执法局湖田中队","20240620-528",2,"未检出","<5","0.24","无","无",0.05,"/","2024.06.22"," 王晓芳"]
[23,"2024.06.20","淄博市公交东站","20240620-529",4,"未检出","<5","0.22","无","无",0.05,"/","2024.06.22"," 王晓芳"]
[24,"2024.06.20","洪三社区","20240620-530",10,"未检出","<5","0.34","无","无",0.04,2.78,"2024.06.22"," 王晓芳"]
[25,"2024.06.24","新村西路140号原市水资办","20240624-531",6,"未检出","<5",0.25,"无","无",0.05,"/","2024.06.26"," 王晓芳"]
[26,"2024.06.24","张店区疾控中心","20240624-532",8,"未检出","<5","0.23","无","无",0.05,"/","2024.06.26"," 王晓芳"]
[27,"2024.06.24","淄博市政务中心","20240624-533",2,"未检出","<5","0.22","无","无",0.06,"/","2024.06.26"," 王晓芳"]
[28,"2024.06.24","盛世康城社区","20240624-534",9,"未检出","<5","0.26","无","无",0.04,"/","2024.06.26"," 王晓芳"]
[29,"2024.06.25","淄博市工商局","20240625-535",2,"未检出","<5","0.32","无","无",0.05,"/","2024.06.27"," 王晓芳"]
[30,"2024.06.25","科技苑物业","20240625-536",5,"未检出","<5","0.29","无","无",0.04,"/","2024.06.27"," 王晓芳"]
[31,"2024.06.25","瑞丰苑社区","20240625-537",9,"未检出","<5","0.27","无","无",0.04,1.37,"2024.06.27"," 王晓芳"]
[32,"2024.06.25","市自来水公司新区营业所","20240625-538",2,"未检出","<5","0.30","无","无",0.05,"/","2024.06.27"," 王晓芳"]
[33,"2024.06.25","祥瑞花园社区","20240625-539",11,"未检出","<5","0.33","无","无",0.04,"/","2024.06.27"," 王晓芳"]
[34,"2024.06.25","世纪花园社区","20240625-540",35,"未检出","<5","0.29","无","无",0.03,"/","2024.06.27"," 王晓芳"]
[35,"2024.06.25","颐臻园社区","20240625-541",7,"未检出","<5","0.26","无","无",0.05,"/","2024.06.27"," 王晓芳"]
[36,"2024.06.26","淄博市体育馆","20240626-542",12,"未检出","<5","0.34","无","无",0.05,"/","2024.06.28"," 王晓芳"]
[37,"2024.06.26","福源汇社区","20240626-543",11,"未检出","<5","0.27","无","无",0.04,"/","2024.06.28"," 王晓芳"]
[38,"2024.06.26","孝妇河湿地公园喷泉广场","20240626-544",7,"未检出","<5","0.29","无","无",0.04,1.51,"2024.06.28"," 王晓芳"]
[39,"2024.06.26","石家社区","20240626-545",9,"未检出","<5","0.31","无","无",0.03,1.29,"2024.06.28"," 王晓芳"]
[40,"2024.06.26","山泉路启星比亚迪4S店","20240626-546",6,"未检出","<5","0.30","无","无",0.05,"/","2024.06.28"," 王晓芳"]
[41,"2024.06.26","福瑞家园社区","20240626-547",28,"未检出","<5","0.25","无","无",0.05,1.65,"2024.06.28"," 王晓芳"]
[42,"2024.06.27","天勤苑社区","20240627-548",8,"未检出","<5","0.29","无","无",0.05,1.63,"2024.06.29"," 王晓芳"]
[43,"2024.06.27","市自来水开发区营业所","20240627-549",15,"未检出","<5","0.15","无","无",0.05,"/","2024.06.29"," 王晓芳"]
[44,"2024.06.27","淄博市十一中","20240627-550",10,"未检出","<5","0.25","无","无",0.03,"/","2024.06.29"," 王晓芳"]
[45,"2024.06.27","丽莎会议中心","20240627-551",19,"未检出","<5","0.28","无","无",0.04,"/","2024.06.29"," 王晓芳"]
[46,"2024.06.27","华侨城警务室","20240627-552",7,"未检出","<5","0.26","无","无",0.04,"/","2024.06.29"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}