{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["9月上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2024.09.02","锦绣花城社区","20240902-737",73,"未检出","<5","0.26","无","无",0.05,1.47,"2024.09.04"," 王晓芳"]
[2,"2024.09.02","市自来水公司铝城营业所","20240902-738",19,"未检出","<5","0.36","无","无",0.04,"/","2024.09.04"," 王晓芳"]
[3,"2024.09.02","经开区后南定村卫生室","20240902-739",2,"未检出","<5","0.33","无","无",0.04,"/","2024.09.04"," 王晓芳"]
[4,"2024.09.02","市自来水公司南定营销服务中心","20240902-740",3,"未检出","<5","0.36","无","无",0.03,2.11,"2024.09.04"," 王晓芳"]
[5,"2024.09.02","张南路101号中石油加油站","20240902-741","未检出","未检出","<5","0.21","无","无",0.03,"/","2024.09.04"," 王晓芳"]
[6,"2024.09.02","西苑社区","20240902-742",10,"未检出","<5","0.25","无","无",0.04,"/","2024.09.04"," 王晓芳"]
[7,"2024.09.03","高新区金晶大道汇驰奔驰4S店","20240903-743",5,"未检出","<5","0.21","无","无",0.03,"/","2024.09.05"," 王晓芳"]
[8,"2024.09.03","金都花园社区","20240903-744",1,"未检出","<5","0.17","无","无",0.03,1.68,"2024.09.05"," 王晓芳"]
[9,"2024.09.03","外商居住区","20240903-745",7,"未检出","<5","0.28","无","无",0.04,"/","2024.09.05"," 王晓芳"]
[10,"2024.09.03","星悦城社区","20240903-746",20,"未检出","<5","0.23","无","无",0.04,1.77,"2024.09.05"," 王晓芳"]
[11,"2024.09.04","淄博市委","20240904-747",5,"未检出","<5","0.23","无","无",0.04,"/","2024.09.06"," 王晓芳"]
[12,"2024.09.04","张店区军休所","20240904-748",2,"未检出","<5","0.27","无","无",0.06,"/","2024.09.06"," 王晓芳"]
[13,"2024.09.04","五里桥生活区","20240904-749",15,"未检出","<5","0.25","无","无",0.04,"/","2024.09.06"," 王晓芳"]
[14,"2024.09.04","张店八中","20240904-750",10,"未检出","<5","0.21","无","无",0.05,"/","2024.09.06"," 王晓芳"]
[15,"2024.09.04","积家村党群服务中心","20240904-751",26,"未检出","<5","0.23","无","无",0.04,1.65,"2024.09.06"," 王晓芳"]
[16,"2024.09.04","明德苑社区","20240904-752",20,"未检出","<5","0.25","无","无",0.03,"/","2024.09.06"," 王晓芳"]
[17,"2024.09.04","淄博市图书馆","20240904-753",5,"未检出","<5","0.19","无","无",0.04,"/","2024.09.06"," 王晓芳"]
[18,"2024.09.09","恒嘉园社区","20240909-754","未检出","未检出","<5","0.24","无","无",0.05,"/","2024.09.11"," 王晓芳"]
[19,"2024.09.09","人民东路小学","20240909-755",10,"未检出","<5","0.21","无","无",0.04,"/","2024.09.11"," 王晓芳"]
[20,"2024.09.09","张店区保安公司","20240909-756",3,"未检出","<5","0.23","无","无",0.05,"/","2024.09.11"," 王晓芳"]
[21,"2024.09.09","润德实业公司","20240909-757","未检出","未检出","<5","0.18","无","无",0.06,"/","2024.09.11"," 王晓芳"]
[22,"2024.09.09","行政执法局湖田中队","20240909-758",5,"未检出","<5","0.22","无","无",0.05,"/","2024.09.11"," 王晓芳"]
[23,"2024.09.09","淄博市公交东站","20240909-759",22,"未检出","<5","0.18","无","无",0.04,"/","2024.09.11"," 王晓芳"]
[24,"2024.09.09","洪三社区","20240909-760",3,"未检出","<5","0.35","无","无",0.03,1.76,"2024.09.11"," 王晓芳"]
[25,"2024.09.10","新村西路140号原市水资办","20240910-761",2,"未检出","<5",0.32,"无","无",0.05,"/","2024.09.12"," 王晓芳"]
[26,"2024.09.10","张店区疾控中心","20240910-762",17,"未检出","<5","0.29","无","无",0.03,"/","2024.09.12"," 王晓芳"]
[27,"2024.09.10","淄博市政务中心","20240910-763",9,"未检出","<5","0.33","无","无",0.04,"/","2024.09.12"," 王晓芳"]
[28,"2024.09.10","盛世康城社区","20240910-764",13,"未检出","<5","0.30","无","无",0.04,"/","2024.09.12"," 王晓芳"]
[29,"2024.09.11","淄博市工商局","20240911-765",11,"未检出","<5","0.24","无","无",0.04,"/","2024.09.13"," 王晓芳"]
[30,"2024.09.11","科技苑物业","20240911-766",10,"未检出","<5","0.19","无","无",0.03,"/","2024.09.13"," 王晓芳"]
[31,"2024.09.11","瑞丰苑社区","20240911-767",9,"未检出","<5","0.27","无","无",0.03,1.63,"2024.09.13"," 王晓芳"]
[32,"2024.09.11","市自来水公司新区营业所","20240911-768",17,"未检出","<5","0.24","无","无",0.05,"/","2024.09.13"," 王晓芳"]
[33,"2024.09.11","祥瑞花园社区","20240911-769",7,"未检出","<5","0.22","无","无",0.05,"/","2024.09.13"," 王晓芳"]
[34,"2024.09.11","世纪花园社区","20240911-770",3,"未检出","<5","0.24","无","无",0.04,"/","2024.09.13"," 王晓芳"]
[35,"2024.09.11","颐臻园社区","20240911-771",7,"未检出","<5","0.22","无","无",0.04,"/","2024.09.13"," 王晓芳"]
[36,"2024.09.12","淄博市体育馆","20240912-772",7,"未检出","<5","0.31","无","无",0.05,"/","2024.09.14"," 王晓芳"]
[37,"2024.09.12","福源汇社区","20240912-773",9,"未检出","<5","0.24","无","无",0.04,"/","2024.09.14"," 王晓芳"]
[38,"2024.09.12","孝妇河湿地公园喷泉广场","20240912-774",1,"未检出","<5","0.26","无","无",0.05,2.21,"2024.09.14"," 王晓芳"]
[39,"2024.09.12","石家社区","20240912-775",10,"未检出","<5","0.29","无","无",0.03,1.89,"2024.09.14"," 王晓芳"]
[40,"2024.09.12","山泉路启星比亚迪4S店","20240912-776",36,"未检出","<5","0.19","无","无",0.04,"/","2024.09.14"," 王晓芳"]
[41,"2024.09.12","福瑞家园社区","20240912-777",7,"未检出","<5","0.25","无","无",0.05,2.17,"2024.09.14"," 王晓芳"]
[42,"2024.09.13","天勤苑社区","20240913-778",16,"未检出","<5","0.31","无","无",0.03,1.83,"2024.09.15"," 王晓芳"]
[43,"2024.09.13","市自来水开发区营业所","20240913-779",5,"未检出","<5","0.29","无","无",0.05,"/","2024.09.15"," 王晓芳"]
[44,"2024.09.13","淄博市十一中","20240913-780",3,"未检出","<5","0.23","无","无",0.04,"/","2024.09.15"," 王晓芳"]
[45,"2024.09.13","丽莎会议中心","20240913-781","未检出","未检出","<5","0.33","无","无",0.03,"/","2024.09.15"," 王晓芳"]
[46,"2024.09.13","华侨城警务室","20240913-782",7,"未检出","<5","0.30","无","无",0.05,"/","2024.09.15"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}