{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["7月下半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2024.08.15","锦绣花城社区","20240815-691",19,"未检出","<5","0.30","无","无",0.06,1.31,"2024.08.17"," 王晓芳"]
[2,"2024.08.15","市自来水公司铝城营业所","20240815-692",6,"未检出","<5","0.28","无","无",0.05,"/","2024.08.17"," 王晓芳"]
[3,"2024.08.15","经开区后南定村卫生室","20240815-693",9,"未检出","<5","0.26","无","无",0.04,"/","2024.08.17"," 王晓芳"]
[4,"2024.08.15","市自来水公司南定营销服务中心","20240815-694",2,"未检出","<5","0.29","无","无",0.06,1.15,"2024.08.17"," 王晓芳"]
[5,"2024.08.15","张南路101号中石油加油站","20240815-695",3,"未检出","<5","0.19","无","无",0.04,"/","2024.08.17"," 王晓芳"]
[6,"2024.08.15","西苑社区","20240815-696",7,"未检出","<5","0.27","无","无",0.05,"/","2024.08.17"," 王晓芳"]
[7,"2024.08.19","高新区金晶大道汇驰奔驰4S店","20240819-697",7,"未检出","<5","0.22","无","无",0.06,"/","2024.08.21"," 王晓芳"]
[8,"2024.08.19","金都花园社区","20240819-698",4,"未检出","<5","0.24","无","无",0.05,1.57,"2024.08.21"," 王晓芳"]
[9,"2024.08.19","外商居住区","20240819-699",13,"未检出","<5","0.27","无","无",0.04,"/","2024.08.21"," 王晓芳"]
[10,"2024.08.19","星悦城社区","20240819-700",16,"未检出","<5","0.21","无","无",0.05,1.69,"2024.08.21"," 王晓芳"]
[11,"2024.08.20","淄博市委","20240820-701",6,"未检出","<5","0.23","无","无",0.05,"/","2024.08.22"," 王晓芳"]
[12,"2024.08.20","张店区军休所","20240820-702",2,"未检出","<5","0.31","无","无",0.04,"/","2024.08.22"," 王晓芳"]
[13,"2024.08.20","五里桥生活区","20240820-703",9,"未检出","<5","0.26","无","无",0.04,"/","2024.08.22"," 王晓芳"]
[14,"2024.08.20","张店八中","20240820-704",11,"未检出","<5","0.19","无","无",0.03,"/","2024.08.22"," 王晓芳"]
[15,"2024.08.20","积家村党群服务中心","20240820-705",19,"未检出","<5","0.23","无","无",0.04,1.66,"2024.08.22"," 王晓芳"]
[16,"2024.08.20","明德苑社区","20240820-706",25,"未检出","<5","0.25","无","无",0.03,"/","2024.08.22"," 王晓芳"]
[17,"2024.08.20","淄博市图书馆","20240820-707",7,"未检出","<5","0.15","无","无",0.04,"/","2024.08.22"," 王晓芳"]
[18,"2024.08.21","恒嘉园社区","20240821-708",3,"未检出","<5","0.24","无","无",0.06,"/","2024.08.23"," 王晓芳"]
[19,"2024.08.21","人民东路小学","20240821-709",11,"未检出","<5","0.20","无","无",0.04,"/","2024.08.23"," 王晓芳"]
[20,"2024.08.21","张店区保安公司","20240821-710",4,"未检出","<5","0.23","无","无",0.05,"/","2024.08.23"," 王晓芳"]
[21,"2024.08.21","润德实业公司","20240821-711","未检出","未检出","<5","0.17","无","无",0.05,"/","2024.08.23"," 王晓芳"]
[22,"2024.08.21","行政执法局湖田中队","20240821-712",3,"未检出","<5","0.23","无","无",0.04,"/","2024.08.23"," 王晓芳"]
[23,"2024.08.21","淄博市公交东站","20240821-713",5,"未检出","<5","0.21","无","无",0.04,"/","2024.08.23"," 王晓芳"]
[24,"2024.08.21","洪三社区","20240821-714",7,"未检出","<5","0.29","无","无",0.03,1.27,"2024.08.23"," 王晓芳"]
[25,"2024.08.26","新村西路140号原市水资办","20240826-715",6,"未检出","<5",0.27,"无","无",0.05,"/","2024.08.28"," 王晓芳"]
[26,"2024.08.26","张店区疾控中心","20240826-716",3,"未检出","<5","0.25","无","无",0.04,"/","2024.08.28"," 王晓芳"]
[27,"2024.08.26","淄博市政务中心","20240826-717",1,"未检出","<5","0.23","无","无",0.04,"/","2024.08.28"," 王晓芳"]
[28,"2024.08.26","盛世康城社区","20240826-718",11,"未检出","<5","0.21","无","无",0.04,"/","2024.08.28"," 王晓芳"]
[29,"2024.08.27","淄博市工商局","20240827-719",17,"未检出","<5","0.26","无","无",0.04,"/","2024.08.29"," 王晓芳"]
[30,"2024.08.27","科技苑物业","20240827-720",13,"未检出","<5","0.19","无","无",0.06,"/","2024.08.29"," 王晓芳"]
[31,"2024.08.27","瑞丰苑社区","20240827-721",12,"未检出","<5","0.25","无","无",0.06,1.55,"2024.08.29"," 王晓芳"]
[32,"2024.08.27","市自来水公司新区营业所","20240827-722",20,"未检出","<5","0.27","无","无",0.05,"/","2024.08.29"," 王晓芳"]
[33,"2024.08.27","祥瑞花园社区","20240827-723",11,"未检出","<5","0.25","无","无",0.05,"/","2024.08.29"," 王晓芳"]
[34,"2024.08.27","世纪花园社区","20240827-724",5,"未检出","<5","0.26","无","无",0.03,"/","2024.08.29"," 王晓芳"]
[35,"2024.08.27","颐臻园社区","20240827-725",9,"未检出","<5","0.25","无","无",0.04,"/","2024.08.29"," 王晓芳"]
[36,"2024.08.28","淄博市体育馆","20240828-726",2,"未检出","<5","0.30","无","无",0.05,"/","2024.08.30"," 王晓芳"]
[37,"2024.08.28","福源汇社区","20240828-727",3,"未检出","<5","0.24","无","无",0.04,"/","2024.08.30"," 王晓芳"]
[38,"2024.08.28","孝妇河湿地公园喷泉广场","20240828-728",31,"未检出","<5","0.21","无","无",0.04,1.53,"2024.08.30"," 王晓芳"]
[39,"2024.08.28","石家社区","20240828-729",11,"未检出","<5","0.31","无","无",0.03,1.37,"2024.08.30"," 王晓芳"]
[40,"2024.08.28","山泉路启星比亚迪4S店","20240828-730",6,"未检出","<5","0.20","无","无",0.05,"/","2024.08.30"," 王晓芳"]
[41,"2024.08.28","福瑞家园社区","20240828-731",9,"未检出","<5","0.25","无","无",0.04,1.62,"2024.08.30"," 王晓芳"]
[42,"2024.08.29","天勤苑社区","20240829-732",23,"未检出","<5","0.28","无","无",0.05,1.45,"2024.08.31"," 王晓芳"]
[43,"2024.08.29","市自来水开发区营业所","20240829-733",7,"未检出","<5","0.29","无","无",0.05,"/","2024.08.31"," 王晓芳"]
[44,"2024.08.29","淄博市十一中","20240829-734",3,"未检出","<5","0.28","无","无",0.04,"/","2024.08.31"," 王晓芳"]
[45,"2024.08.29","丽莎会议中心","20240829-735",4,"未检出","<5","0.27","无","无",0.03,"/","2024.08.31"," 王晓芳"]
[46,"2024.08.29","华侨城警务室","20240829-736",2,"未检出","<5","0.25","无","无",0.05,"/","2024.08.31"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}