{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["09上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2025.09.01","新村西路140号原市水资办","20250901-0737",30,"未检出","<5","0.34","无","无",0.05,"/","2025.09.03"," 王晓芳"]
[2,"2025.09.01","淄博市政务中心","20250901-0738",6,"未检出","<5","0.32","无","无",0.05,"/","2025.09.03"," 王晓芳"]
[3,"2025.09.01","张店区疾控中心","20250901-0739",19,"未检出","<5","0.29","无","无",0.03,"/","2025.09.03"," 王晓芳"]
[4,"2025.09.01","西苑社区","20250901-0740",5,"未检出","<5","0.31","无","无",0.04,"/","2025.09.03"," 王晓芳"]
[5,"2025.09.01","五公里党群站","20250901-0741",25,"未检出","<5","0.21","无","无",0.04,1.15,"2025.09.03"," 王晓芳"]
[6,"2025.09.01","   市自来水公司南定营销服务中心","20250901-0742",10,"未检出","<5","0.34","无","无",0.03,1.03,"2025.09.03"," 王晓芳"]
[7,"2025.09.01","市自来水公司铝城营业所","20250901-0743",26,"未检出","<5","0.36","无","无",0.05,"/","2025.09.03"," 王晓芳"]
[8,"2025.09.01","经开区后南定村卫生室","20250901-0744",12,"未检出","<5","0.33","无","无",0.04,"/","2025.09.03"," 王晓芳"]
[9,"2025.09.01","张南路101号中石油加油站","20250901-0745",7,"未检出","<5","0.20","无","无",0.03,"/","2025.09.03"," 王晓芳"]
[10,"2025.09.01","山泉路启星比亚迪4S店","20250901-0746",13,"未检出","<5","0.31","无","无",0.03,"/","2025.09.03"," 王晓芳"]
[11,"2025.09.02","天勤苑社区","20250902-0747",11,"未检出","<5","0.26","无","无",0.03,1.11,"2025.09.04"," 王晓芳"]
[12,"2025.09.02","高新区金晶大道汇驰奔驰4S店","20250902-0748",5,"未检出","<5","0.33","无","无",0.04,"/","2025.09.04"," 王晓芳"]
[13,"2025.09.02","金都花园社区","20250902-0749",4,"未检出","<5","0.15","无","无",0.05,1.35,"2025.09.04"," 王晓芳"]
[14,"2025.09.02","星悦城社区","20250902-0750",17,"未检出","<5","0.23","无","无",0.04,1.27,"2025.09.04"," 王晓芳"]
[15,"2025.09.02","外商居住区","20250902-0751",1,"未检出","<5","0.25","无","无",0.03,"/","2025.09.04"," 王晓芳"]
[16,"2025.09.02","市自来水开发区营业所","20250902-0752",6,"未检出","<5","0.24","无","无",0.04,"/","2025.09.04"," 王晓芳"]
[17,"2025.09.02","淄博市十一中","20250902-0753",2,"未检出","<5","0.26","无","无",0.04,"/","2025.09.04"," 王晓芳"]
[18,"2025.09.02","丽莎会议中心","20250902-0754",21,"未检出","<5","0.20","无","无",0.03,"/","2025.09.04"," 王晓芳"]
[19,"2025.09.02","华侨城警务室","20250902-0755",13,"未检出","<5","0.35","无","无",0.03,"/","2025.09.04"," 王晓芳"]
[20,"2025.09.03","淄博市委","20250903-0756","未检出","未检出","<5","0.35","无","无",0.04,"/","2025.09.05"," 王晓芳"]
[21,"2025.09.03","张店区军休所","20250903-0757",17,"未检出","<5","0.32","无","无",0.03,"/","2025.09.05"," 王晓芳"]
[22,"2025.09.03","五里桥生活区","20250903-0758",2,"未检出","<5","0.21","无","无",0.04,"/","2025.09.05"," 王晓芳"]
[23,"2025.09.03","祥瑞花园社区","20250903-0759",27,"未检出","<5","0.19","无","无",0.04,"/","2025.09.05"," 王晓芳"]
[24,"2025.09.03","张店八中","20250903-0760",10,"未检出","<5","0.20","无","无",0.03,"/","2025.09.05"," 王晓芳"]
[25,"2025.09.03","淄博市图书馆","20250903-0761",8,"未检出","<5",{"v":0.3,"d":"0.30"},"无","无",0.03,"/","2025.09.05"," 王晓芳"]
[26,"2025.09.03","积家村党群服务中心","20250903-0762",3,"未检出","<5","0.32","无","无",0.05,1.29,"2025.09.05"," 王晓芳"]
[27,"2025.09.03","明德苑社区","20250903-0763",6,"未检出","<5","0.19","无","无",0.02,"/","2025.09.05"," 王晓芳"]
[28,"2025.09.08","恒嘉园社区","20250908-0764",2,"未检出","<5","0.28","无","无",0.05,"/","2025.09.10"," 王晓芳"]
[29,"2025.09.08","人民东路小学","20250908-0765",6,"未检出","<5","0.33","无","无",0.03,"/","2025.09.10"," 王晓芳"]
[30,"2025.09.08","张店区保安公司","20250908-0766",5,"未检出","<5","0.22","无","无",0.04,"/","2025.09.10"," 王晓芳"]
[31,"2025.09.08","润德实业公司","20250908-0767",6,"未检出","<5","0.27","无","无",0.06,"/","2025.09.10"," 王晓芳"]
[32,"2025.09.08","行政执法局湖田中队","20250908-0768",5,"未检出","<5","0.29","无","无",0.03,"/","2025.09.10"," 王晓芳"]
[33,"2025.09.08","淄博市公交东站","20250908-0769","未检出","未检出","<5","0.21","无","无",0.04,"/","2025.09.10"," 王晓芳"]
[34,"2025.09.08","洪三社区","20250908-0770","未检出","未检出","<5","0.34","无","无",0.03,1.21,"2025.09.10"," 王晓芳"]
[35,"2025.09.15","淄博市工商局","20250915-0771","未检出","未检出","<5","0.33","无","无",0.04,"/","2025.09.17"," 王晓芳"]
[36,"2025.09.15","市自来水公司新区营业所","20250915-0772","未检出","未检出","<5","0.21","无","无",0.05,"/","2025.09.17"," 王晓芳"]
[37,"2025.09.15","颐臻园社区","20250915-0773",7,"未检出","<5","0.24","无","无",0.03,"/","2025.09.17"," 王晓芳"]
[38,"2025.09.15","世纪花园社区","20250915-0774",1,"未检出","<5","0.30","无","无",0.04,"/","2025.09.17"," 王晓芳"]
[39,"2025.09.15","瑞丰苑社区","20250915-0775",4,"未检出","<5","0.30","无","无",0.05,1.22,"2025.09.17"," 王晓芳"]
[40,"2025.09.15","科技苑物业","20250915-0776",15,"未检出","<5","0.34","无","无",0.03,"/","2025.09.17"," 王晓芳"]
[41,"2025.09.16","淄博市体育馆","20250916-0777","未检出","未检出","<5","0.26","无","无",0.03,"/","2025.09.18"," 王晓芳"]
[42,"2025.09.16","福源汇社区","20250916-0778",2,"未检出","<5","0.32","无","无",0.04,"/","2025.09.18"," 王晓芳"]
[43,"2025.09.16","孝妇河湿地公园喷泉广场","20250916-0779",3,"未检出","<5","0.29","无","无",0.04,1.33,"2025.09.18"," 王晓芳"]
[44,"2025.09.16","石家社区","20250916-0780",1,"未检出","<5","0.28","无","无",0.03,1.16,"2025.09.18"," 王晓芳"]
[45,"2025.09.16","盛世康城社区","20250916-0781",5,"未检出","<5","0.31","无","无",0.04,"/","2025.09.18"," 王晓芳"]
[46,"2025.09.16","福瑞家园社区","20250916-0782",2,"未检出","<5","0.28","无","无",0.05,{"v":1.3,"d":"1.30"},"2025.09.18"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}